## Slide 1: Title 5 Plan Review: A Hands On Approach
Andrew Osei and Brian Dudley, MassDEP
October 21, 2021
2021 MHOA Educational conference, FALMOUTH, MA

## Slide 2: DISCLAIMERS
Any proprietary technology mentioned in this presentation is used purely as an example and its inclusion does not constitute a comment on or endorsement of the technology by the presenter or MassDEP.
This presentation relates solely to 310 CMR 15.000, Title 5 of the State Environmental Code. Many municipalities have regulations that are more restrictive than Title 5.

## Slide 3
Objectives
Septic system plan basics
Non-conventional
systems
Checklists
Hands-on exercise
Deficiency and approval
letters
Wrap-up

## Slide 4: Septic System Plan Basics

## Slide 5: Septic System Components
Building sewer
Grease trap*
Septic tank
Alternative technology*
Pump chamber (pre/post)*
Distribution box*
Soil absorption system
Vents and inspection port

## Slide 6: Design Plan Components
Plan view of the system showing entire lot and all components
Profile of the system
Details of the components
Soil evaluation and percolation testing information
  SE and certification statement
  BOH witness

## Slide 7: Soil Information
Within 60 days after soil testing,
  SE of record must certify soil results to BOH
  SE of record must submit soil results to BOH
Plans should include:
  All deep hole locations and logs (incl. elev.)
  Perc test locations and logs (incl. elev.)
  Soil evaluator of record and BOH witness as well as other important information

## Slide 8: Plan and Profile
Site plan
  Property lines/ROWs
  Buildings/structures and Paved surfaces
Profile
  To scale
  Elevations
Designer Stamp: PE or RS (PLS stamp?)

## Slide 9: System Components 1:
Building Sewer
Material
Slope
Access (change in direction)
Septic Tank
Size/Compartment(s)
Inverts
Material
Tees/baffles/filter
Inlet/outlet drop
Accessibility

## Slide 10: System Components 2:
To septic tank
  Pump type
  Sizing/compartments
To d-box or SAS
  Material
  Storage
  Alarms
  Dual pumps?
Material
Sump size
Level outlets
Pump Chamber
Distribution Box

## Slide 11: System Components 3 – SASs:
Type – bed/field, trench, gallery/pit/chamber
LTAR
Size
Calculations shown – Mounding calculations?
Reductions taken?
Adequate depth to groundwater
Venting
Inspection port

## Slide 12: Non-conventional Systems

## Slide 13: Non-conventional System Designs:
Tight tank
Shared system (cluster or not)
Nitrogen aggregation approval
Alternative technology
  Secondary treatment unit (STU)
  Patented sand filter
  Drip dispersal system
  Alternative SAS

## Slide 14: Alternative Technology Considerations:
Type of MassDEP issued approval
Model of the technology
Compliance with terms and conditions of approvals
  Best feasible alternative identification and siting
  Owner acknowledgement
  Deed notice

## Slide 15: Checklists

## Slide 16
WHY?
WHAT?
HOW?
WHO?

## Slide 17: Who Benefits from Checklists?
Health Department staff
Board of Health members
Consultants to the Dept/BOH
Designers
Installers
Property owners/public

## Slide 18: Why Use a Checklist?
Multiple programs
Septic
Food
Housing
Pools
Public health/nursing
Emergency preparedness
Multiple reviewers
BOH staff
Town/City engineering staff
Consultants
Others
  ConCom
  Building Dept.
  Etc.

## Slide 19: Some things to Include in a Checklist(s):
Regulations
  Title 5
  Local bylaw
Design flow
Soil testing
Component standards
SAS design
Tight tanks
Greywater systems
Alternative technologies
  Standard conditions
Nitrogen aggregation approvals
Shared systems
Timelines for review

## Slide 20: How Do You Create a Checklist?
Make your own from scratch
310 CMR 15.220, especially 15.220(4)
Barnstable County Health Department
MassDEP
  Recommended:
  Start with MassDEP’s revised checklist (Sep 2019) and remember to include any local bylaws/regulations

## Slide 21: Deficiency and Approval Letters

## Slide 22: Standard Letters
deficiency
Deficiency date
Meeting or hearing date
Plan name, date & designer
Deficiencies
  Listed & detailed
  Regulatory, policy, guidance & approval citations
approval
Approval date
Meeting or hearing date
Plan name, date & designer
Special conditions
  Coordination with BOH agent
  Flagging of components
  Watertightness testing, etc.

## Slide 23: Wrap-Up

## Slide 24: Common Barriers to Compliant Systems
Poor soils;
Ledge;
Small lot;
Wetlands;
On-site well; or
Any combination/permutation of the above.

## Slide 25: Hands On Exercise

## Slide 26: Acknowledgements and Thanks
Demo Plan preparation
Kirk FitzPatrick, E.I.T.
Civil Solutions
Westford
Kevin Richie, P.E.
Civil Solutions
Westford

## Slide 27: There are only two rules for upgrades…..
Rule # 1
Full compliance is always the goal!
[310 CMR 15.404(1)]
Rule # 2
Don’t forget Rule #1!

## Slide 28
?
?
?
?
Questions?

## Slide 29: MassDEP REGIONAL CONTACTS
SERO
Brian Dudley (Cape) Brett Rowe (SE MA)
brian.dudley@mass.gov brett.rowe@mass.gov
508-946-2814 508-946-2754
WERO
John Bourcier Dan Kurpaska
john.bourcier@mass.gov daniel.kurpaska@mass.gov
413-755-2112 413-755-2274
Matt Sokop
matthew.sokop@mass.gov
413-755-2218
CERO
David Boyer
david.boyer@mass.gov
508-767-2823
NERO
Wastewater Info Line
978-694-3215
Claire Golden
claire.golden@mass.gov
978-694-3244